## General
D20 ME, MEII and MX QC Document
Revisions
Revision | Date | Description |  | Name
----- | 2016-05-04 | Initial document |  | RBC
1 | 2017-03-27 | Added Accumulator Freeze settings to be checked. |  | ARF
2 | 2017-04-13 | Revised Communication Watchdog examples |  | ARF
3 | 2017-07-19 | Added columns for Python script output |  | MAC

## D20++ QC Doc
First Energy D20++ QC Checklist
Substation Name
C:/Users/clbishop/Documents/GitHub/FE-D20_Checker/Example D20 XML/D20M++/PLVLY_Q D20M++.xml
Config Name |  | Revision Text from Config
Config Engineers Initials in Cell H6, Q4 Reviewers initials in cell J6
NAME | APPLICATION | TABLE | COLUMN | SETTING | Q3 | Q4 | Some Python Values
OLD CONFIG
DNP DCA | B023_PNT | DEVICE CONFIGURATION | DCA Object Type | Number of REAL Device Points
Binary Input
|  | Use Pull Down under "DCA Object Type" for point type. Insert real device points in colum F |  |  |  |  | Binary Input | Binary Output
[7 empty] | Binary Output | Running Counter
[7 empty] | Running Counter | Frozen Counter
[7 empty] | Frozen Counter | Analog Input
Analog Input 16
NEW CONFIG
DNP DCA | B023_PNT | DEVICE CONFIGURATION | DCA Object Type | Number of REAL Device Points
|  |  | Analog Input | 18
|  | Use Pull Down under "DCA Object Type" for point type. Insert real device points in colum F | Analog Input | 11
|  |  | Running Counter | 4
|  |  | Analog Input | 42
DNP DCA | B023_CFG | DCA CONFIGURATION | RESTART DELAY | 10 |  |  | 10
DNP DCA | B023_DEV | DEVICE CONFIGURATION | POLL INTERVAL | 5 sec |  |  | 5
DNP DCA | B023_DEV | DEVICE CONFIGURATION | INTEGRITY POLL INTERVAL | 0 |  |  | 0
DNP DCA | B023_DEV | DEVICE CONFIGURATION | OFFLINE AFTER FAIL | OFFLINE AFTER CHAN. FAIL |  |  | Off-line after chan fail
DNP DCA | B023_DEV | DEVICE CONFIGURATION | FAILURES FOR BAD CHAN. | 3 (minimum) |  |  | 3
DNP DCA | B023_DEV | DEVICE CONFIGURATION | TIMESYNCING | DISABLE |  |  | Disable
HARRIS DCA | A020_SRU | SRU TABLE | RE-INIT INTERVAL | 5 |  |  | Application A020 is disabled for this site.
SYSTEM PT. DB B008 | A0083 | CALCULATOR DTA | DCA POINTS | DEVICES = 0 |  |  | D20 Calculator: Digital Inputs table does not have event types.
SYSTEM PT. DB B008 | ALL DCAs | POINT DESCRIPTION | DEVICES | DEVICE DESCRIPTION & ADDR.
System Point Database DNP Instance Totalizer
Use this for each instance just as a check of your work
Insert Values in the red cells below for each DNP instance of your System Point Database |  | Total DI's: |  | These are the values that need to be in the System Point Database. These values include Pseudo Points
Total DO's:
Total AI's:
Total DV's:
24 Analog in for Satec, 21 Analog in for Bitronic, Mixture of points for RTACS and other devices.
Analog Inputs | Digital Inputs | Digital Outputs | Counter Inputs | Devices
0 | 3 | 9 |  | 0
WESMAINT ll | B014MCFG | BUFFER CONFIGURATION | SOE BUFFER SIZE | 500 |  |  | 500
WESMAINT ll | B014MCFG | BUFFER CONFIGURATION | SOE LOCATION | NVRAM |  |  | NVRAM
WESMAINT ll | WM_TIME | Daylight Savings Time | Standard UTC Offset | 0 |  |  | 0
WESMAINT ll | WM_TIME | Daylight Savings Time | DST Offset | 0 |  |  | 0
WESMAINT ll | B014USER | USER CONFIGURATION | USER NAME |  |  |  | Please refer to the SGConfig.
WESMAINT ll | B014USER | USER CONFIGURATION | PASSWORD
WESMAINT ll | B014USER | USER CONFIGURATION | CONTROL PASSWORD
WESMAINT ll | WWELCOME | WELCOME MESSAGE | Row =15, Inverse | NEW LOGIN
WESMAINT ll | WWELCOME | WELCOME MESSAGE
| Row | Message
| 5 | PLEASANT VALLEY SUBSTATION SAB0605/03 |  | Insert new device welcome screen text in Cell C76
| 7 | Port 1 - DNP3.0 SEL3530 RTAC2, 9600 baud
| 8 | Port 2 - DNP DPA WCC, MPLS 9600 Baud
| 9 | Port 3 - Spare
| 10 | Port 4 - DNP3.0 DPA SAM-900 HMI, 9600 baud
| 11 | Port 5 - DNP3.0 SEL3530 RTAC1, 9600 baud
| 12 | Port 6 - DNP3.0 Q-22 ION Meter, 9600 baud
| 13 | Port 7 - Spare
| 15 | NEW LOGIN:
BRIDGEMAN | B015 | CONFIGURATION TABLE | Number of RX Buffers | 10 |  |  | 15
|  | LOCAL | LOCAL | LOCAL
BRIDGEMAN | B015 | Application Address | Data Link Channel | LAN Address (Hex) |  |  | Corresponding COM Port
|  | 5 | 0 | 5 |  |  | COM5
|  | 6 | 1 | 6 |  |  | COM6
|  | 1089 | 2 | 441 |  |  | COM2
|  | 501 | 3 | 1F5 |  |  | COM4
|  | 10 | 4 | A |  |  | COM1
|  | REMOTE | REMOTE | REMOTE
BRIDGEMAN | B015 | Application Address | Data Link channel | LAN Address (Hex) |  |  | Corresponding COM Port
|  | 51 | 0 | 33 |  |  | COM5
|  | 61 | 1 | 3D |  |  | COM6
|  | 10 | 2 | A |  |  | COM2
|  | 500 | 3 | 1F4 |  |  | COM4
|  | 11 | 4 | B |  |  | COM1
Comm Watchdog | A026_CFG | ***** See Examples below *****
Record Point | Point Type | System Point | Comm Event Point | Normal State |  |  | **May not contain all values. If you need them all, please refer to the SGConfig**
0 | Digital Input | (000001) Q-1-JR-PV | (000145) D20 S1 Comm Watchdog On/Off Line | Off
1 | Digital Input | (000065) B17 Q-72-IP-B BF | (000146) D20 S2 Comm Watchdog On/Off Line | Off
2 | Analog Input | (000001) Spare 1 | (000147) D20 A1 Comm Watchdog On/Off Line | Off
3 | Analog Input | (000033) Q-3-PV-BUS KV | (000148) D20 A2 Comm Watchdog On/Off Line | Off
4 | Digital Output | (000001) Q-1-JR-PV | (000149) D20 K1 Comm Watchdog On/Off Line | Off
5 | Digital Input | (000129) Status pt. # 129 | (000150) D20 C1 Comm Watchdog On/Off Line | Off
6 | Analog Input | (000130) BITRONICS Q-1-FW-PV RTAC2 P12 Ph A Volts | (000151) Q-1 Bitronics Comm Watchdog | Off
7 | Analog Input | (000134) SATEC Q-3-FW-PV RTAC2 P12 Ph A Volts | (000152) Q-3-FW-PV Satec Meter Comm Watchdog | Off
8 | Analog Input | (000080) Q-22-PV-WAK RTAC1 COM32 Ph B Amps | (000153) RTAC1 Comm Watchdog | Off
9 | Analog Input | (000096) Total MW | (000154) Q-22 ION8600C Comm Watchdog | Off
10 | Analog Input | (000138) SATEC Q-4-FW-PV RTAC2 P12 Ph A Volts | (000156) Q-4-FW-PV Satec Meter Comm WD | Off
11 | Analog Input | (000114) SATEC#3 Q-1-JR-PV RTAC2 P11 Ph A Volts | (000157) Q-1-JR-PV Satec Meter Comm WD | Off
12 | Analog Input | (000122) SATEC#4 Q-3-JR-PV RTAC2 P11 Ph A Volts | (000158) Q-3-JR-PV Satec Meter Comm WD | Off
13 | Analog Input | (000118) SATEC#5 Q-4-JR-PV RTAC2 P11 Ph A Volts | (000159) Q-4-JR-PV Satec Meter Comm WD | Off
14 | Analog Input | (000126) SATEC#6 PV-WAkron Q22 RTAC2 P11 PhA Volt | (000160) Q-22-PV-WAK Satec Meter Comm WD | Off
15 | Analog Input | (000080) Q-22-PV-WAK RTAC1 COM32 Ph B Amps | (000161) SEL421 PR/WAK RTAC COM32 WD | Off
16 | Analog Input | (000083) Q-21-PV-HP RTAC1 COM20 Ph B Amps | (000162) Q-21-PV-HP RTAC1 COM20 WD | Off
17 | Analog Input | (000081) Q-3-FW-PV RTAC1 COM5 Ph B Amps | (000163) Q-3-FW-PV SEL421 RTAC1 COM5 WD | Off
18 | Analog Input | (000082) Q-4-FW-PV RTAC1 COM7 Ph B Amps | (000164) Q-4-FW-PV SEL421 RTAC1 COM7 WD | Off
19 | Analog Input | (000084) Q-1-JR-PV RTAC1 COM22 Ph B Amps | (000165) Q-1-JR-PV SEL421 RTAC1 COM22 WD | Off
20 | Analog Input | (000085) Q-3-JR-PV RTAC1 COM26 Ph B Amps | (000166) Q-3-JR-PV SEL421 RTAC1 COM26 WD | Off
21 | Analog Input | (000086) Q-4-JR-PV RTAC1 COM29 Ph B Amps | (000167) Q-4-JR-PV SEL421 RTAC1 COM29 WD | Off
22 | Analog Input | (000150) SATEC Q-2-FW-PV Ph A Volts | (000168) Fowles - PV Q2 Satec Meter Comm WD | Off
23 | Analog Input | (000142) SATEC HARDNG-PV Q12 RTAC2 P13 Ph A Volts | (000169) Harding - PV Q12 Satec Meter Comm WD | Off
24 | Analog Input | (000146) SATEC HARDNG-PV Q13 RTAC2 P13 Ph A Volts | (000170) Harding - PV Q13 Satec Meter Comm WD | Off
25 | Analog Input | (000088) Fowles-PV Q2 RTAC1 COM11 Ph B Amps | (000171) Q-2-FW-PV SEL421 RTAC1 COM11 WD | Off
26 | Analog Input | (000090) Hardng-PV Q12 RTAC1 COM11 Ph B Amps | (000172) Q-12-HD-PV SEL421 RTAC1 COM12 WD | Off
27 | Analog Input | (000113) Harding - PV Q13 Ph B Amps RTAC2 P7 | (000173) Q-13-HD-PV SEL421 RTAC2 COM7 WD | Off
28 | Analog Input | (000114) SATEC#3 Q-1-JR-PV RTAC2 P11 Ph A Volts | (000174) SEL3530 RTAC2 COMM WD | Off
COMMUNICATION WD | A026DCA | DCA CONFIGURATION | SOE ENABLE | YES |  |  | Yes
COMMUNICATION WD | A026DCA | DCA CONFIGURATION | COS ENABLE | YES |  |  | Yes
SATEC Meter Comm
DNP Datalink | B013_CFG | Port Configuration | Baud Rate | 9600 |  |  | Please refer to the SGConfig for the Baud Rate.
ACCUM. FREEZE | A030CFG | DTA MISC PARAMETERS | TIME SYNC WAIT | 30000 |  |  | 30000
ACCUM. FREEZE | A030CFG | STATUS/ACC FREEZE | ALL COLUMNS | Empty (No Values) |  |  | There are no STATUS/ACC FREEZE values.
ACCUM. FREEZE | A030CFG | ACC FREEZE/CONTROLS | ALL COLUMNS | Empty (No Values) |  |  | There are no ACC FREEZE/CONTROLS values.
DNP DPA | B021CFG | DPA CONFIGURATION | DATALINK CONFIRM | Disabled |  |  | Disabled
DNP DPA | B021CFG | Unsolicited Responses | Idle Report Period | 3000 |  |  | 3000
HARRIS DPA | A003MT01 | DIGITAL INPUT MAP | SOE | NO |  |  | Application A003 is disabled for this site.
HARRIS DPA | A003_LRU | LRU CONFIGURATION | OFFLINE CONDITION | ALL POINTS |  |  | Application A003 is disabled for this site.
Optional Settings if Needed
HARRIS DPA | A003MT02 | DIGITAL OUTPUT MAP | CONTACT DUR/BASE TIME | 500 |  |  | Application A003 is disabled for this site.
Check Scaling for the Harris analog points. Fault Distance and TR Winding Temp should be as shown above. All other scaling factors should be as the Volts are shown in the above graphic. | [6 empty] | User Check
Revenue Meter Settings
(Derived from Mansfield Rev Meter config that had minimal errors to revenue meters)
BRIDGEMAN | B015_RAT | REMOTE APPLICATION | TX DELAY TO APPL. | 250 |  |  | Refer to the SGConfig for TX DELAY TO APPL. values.
DNP Datalink | B013_CFG | Port Configuration | DCD, RTS, & CTS | Disable |  |  | Disabled
|  |  | DCD to RX enable time | 0 |  |  | 8
|  |  | RTS Preamble | 35 |  |  | 40
|  |  | RTS Postamble | 15 |  |  | 20
|  |  | Max Frame Size | 249 |  |  | 249
|  |  | Transmit Retries | 3 |  |  | 3
|  |  | Transmit Buffers | 10 |  |  | 10
|  |  | Receive Buffers | 10 |  |  | 10
|  |  | Confirm Timeout | 400 |  |  | 2000
|  |  | Response Timeout | 400 |  |  | 2000
DNP DCA | B023_DEV | DEVICE CONFIGURATION | Data Link CFM Required | Confirm Required |  |  | Confirm Not Required
After the Config is done, go back and make sure the WinPoints in the Points List were updated to reflect the new equipment or changes and match what is in the Config File. | [6 empty] | User Check
Does this config have an HMI associated with it? If so go back and make sure your WinPoints are correct in the points list for any revisions made in the config. | [6 empty] | User Check

## ME++ Pseudo points
ME++ DEFAULT PSEUDOS
| Analog | Digital Input | Digital Output
1 | ONE WAY TRANSMISSION DELAY | Global DEVICES DISABLED | Global DISABLE ALL DEV
2 | # OF SUCCESSFUL TRANS W/DEV | Global POLLING DISABLED ALL DEV | Global DISABLE POLLS TO ALL DEV
3 | # OF FAILURES | Global DISABLE UNSOL RESP ALL DEV | Global DISABLE UNSOL RESP
4 | PRESENT CHANNEL | ENABLED/DISABLED DEVICE | Global POLL ALL DEV FOR CLSS DATA
5 | % OF SUCCESSFUL TRANSACTIONS | POLLING ENABLED/DISABLED | Global POLL ALL DEV FOR INTG DATA
6 |  | UNSOL RESP ENABLED/DISABLED | Global RESTART ALL DEV
7 |  | POLL FOR DATA | Global TIMESYNC ALL DEV
8 |  | REMOTE RESTART | Global CLEAR CHANNEL
9 |  | TIME SYNC REMOTE | Global CLEAR COMM STATISTIC
10 |  | PROPAGATION DELAY MEASURE | DEVICE ENABLED
11 |  | PRI COMM CHANNEL STATUS | SCHEDULED POLLS ENABLED
12 |  | SEC COMM CHANNEL STATUS | UNSOLICITED RESP ENABLED
13 |  | PRI CHANNEL IN USE | POLL DEV FOR CLASS DATA
14 |  | SEC CHANNEL IN USE | POLL DEV FOR INTEG DATA
15 |  | IIN RESTART BIT STATE | DEVICE RESTART
16 |  | IIN TROUBLE BIT STATE | TIMESYNC IN PROGRESS
17 |  |  | PROPAGATION DELAY IN PROG
18 |  |  | FORCE NEXT COM CHANNEL
19 |  |  | CLEAR COMM STATISTIC