## General
D20 ME, MEII and MX QC Document
Revisions
Revision | Date | Description |  | Name
----- | 2016-05-04 | Initial document |  | RBC
1 | 2017-03-27 | Added Accumulator Freeze settings to be checked. |  | ARF
2 | 2017-04-13 | Revised Communication Watchdog examples |  | ARF

## D20++ QC Doc
this is test |  |  | First Energy D20++ QC Checklist
Substation Name
| Config Name |  | Revision Text from Config
Config Engineers Initials in Cell H6, Q4 Reviewers initials in cell J6
| NAME | APPLICATION | TABLE | COLUMN | SETTING | Q3 | Q4
OLD CONFIG
| DNP DCA | B023_PNT | DEVICE CONFIGURATION | DCA Object Type | Number of REAL Device Points
Binary Input
|  |  | Use Pull Down under "DCA Object Type" for point type. Insert real device points in colum F |  |  |  |  | Binary Input | Binary Output
[8 empty] | Binary Output | Running Counter
[8 empty] | Running Counter | Frozen Counter
[8 empty] | Frozen Counter | Analog Input
Analog Input 16
NEW CONFIG
| DNP DCA | B023_PNT | DEVICE CONFIGURATION | DCA Object Type | Number of REAL Device Points
Use Pull Down under "DCA Object Type" for point type. Insert real device points in colum F
| DNP DCA | B023_CFG | DCA CONFIGURATION | RESTART DELAY | 10
| DNP DCA | B023_DEV | DEVICE CONFIGURATION | POLL INTERVAL | 5 sec
| DNP DCA | B023_DEV | DEVICE CONFIGURATION | INTEGRITY POLL INTERVAL | 0
| DNP DCA | B023_DEV | DEVICE CONFIGURATION | OFFLINE AFTER FAIL | OFFLINE AFTER CHAN. FAIL
| DNP DCA | B023_DEV | DEVICE CONFIGURATION | FAILURES FOR BAD CHAN. | 3 (minimum)
| DNP DCA | B023_DEV | DEVICE CONFIGURATION | TIMESYNCING | DISABLE
| HARRIS DCA | A020_SRU | SRU TABLE | RE-INIT INTERVAL | 5
| SYSTEM PT. DB B008 | A0083 | CALCULATOR DTA | DCA POINTS | DEVICES = 0
| SYSTEM PT. DB B008 | ALL DCAs | POINT DESCRIPTION | DEVICES | DEVICE DESCRIPTION & ADDR.
System Point Database DNP Instance Totalizer
Use this for each instance just as a check of your work
| Insert Values in the red cells below for each DNP instance of your System Point Database |  | Total DI's: |  | These are the values that need to be in the System Point Database. These values include Pseudo Points
Total DO's:
Total AI's:
Total DV's:
24 Analog in for Satec, 21 Analog in for Bitronic, Mixture of points for RTACS and other devices.
| Analog Inputs | Digital Inputs | Digital Outputs | Counter Inputs | Devices
| 0 | 3 | 9 |  | 0
| WESMAINT ll | B014MCFG | BUFFER CONFIGURATION | SOE BUFFER SIZE | 500
| WESMAINT ll | B014MCFG | BUFFER CONFIGURATION | SOE LOCATION | NVRAM
| WESMAINT ll | WM_TIME | Daylight Savings Time | Standard UTC Offset | 0
| WESMAINT ll | WM_TIME | Daylight Savings Time | DST Offset | 0
| WESMAINT ll | B014USER | USER CONFIGURATION | USER NAME
| WESMAINT ll | B014USER | USER CONFIGURATION | PASSWORD
| WESMAINT ll | B014USER | USER CONFIGURATION | CONTROL PASSWORD
| WESMAINT ll | WWELCOME | WELCOME MESSAGE | Row =15, Inverse | NEW LOGIN
| WESMAINT ll | WWELCOME | WELCOME MESSAGE
Insert new device welcome screen text in Cell C76
| BRIDGEMAN | B015 | CONFIGURATION TABLE | Number of RX Buffers | 10
|  |  | LOCAL | LOCAL | LOCAL
| BRIDGEMAN | B015 | Application Address | Data Link Channel | LAN Address (Hex)
|  |  | REMOTE | REMOTE | REMOTE
| BRIDGEMAN | B015 | Application Address | Data Link channel | LAN Address (Hex)
| Comm Watchdog | A026_CFG | ***** See Examples below *****
| COMMUNICATION WD | A026DCA | DCA CONFIGURATION | SOE ENABLE | YES
| COMMUNICATION WD | A026DCA | DCA CONFIGURATION | COS ENABLE | YES
SATEC Meter Comm
| DNP Datalink | B013_CFG | Port Configuration | Baud Rate | 9600
| ACCUM. FREEZE | A030CFG | DTA MISC PARAMETERS | TIME SYNC WAIT | 30000
| ACCUM. FREEZE | A030CFG | STATUS/ACC FREEZE | ALL COLUMNS | Empty (No Values)
| ACCUM. FREEZE | A030CFG | ACC FREEZE/CONTROLS | ALL COLUMNS | Empty (No Values)
| DNP DPA | B021CFG | DPA CONFIGURATION | DATALINK CONFIRM | Disabled
| DNP DPA | B021CFG | Unsolicited Responses | Idle Report Period | 3000
| HARRIS DPA | A003MT01 | DIGITAL INPUT MAP | SOE | NO
| HARRIS DPA | A003_LRU | LRU CONFIGURATION | OFFLINE CONDITION | ALL POINTS
Optional Settings if Needed
| HARRIS DPA | A003MT02 | DIGITAL OUTPUT MAP | CONTACT DUR/BASE TIME | 500
Check Scaling for the Harris analog points. Fault Distance and TR Winding Temp should be as shown above. All other scaling factors should be as the Volts are shown in the above graphic.
Revenue Meter Settings
(Derived from Mansfield Rev Meter config that had minimal errors to revenue meters)
| BRIDGEMAN | B015_RAT | REMOTE APPLICATION | TX DELAY TO APPL. | 250
| DNP Datalink | B013_CFG | Port Configuration | DCD, RTS, & CTS | Disable
|  |  |  | DCD to RX enable time | 0
|  |  |  | RTS Preamble | 35
|  |  |  | RTS Postamble | 15
|  |  |  | Max Frame Size | 249
|  |  |  | Transmit Retries | 3
|  |  |  | Transmit Buffers | 10
|  |  |  | Receive Buffers | 10
|  |  |  | Confirm Timeout | 400
|  |  |  | Response Timeout | 400
| DNP DCA | B023_DEV | DEVICE CONFIGURATION | Data Link CFM Required | Confirm Required
After the Config is done, go back and make sure the WinPoints in the Points List were updated to reflect the new equipment or changes and match what is in the Config File.
Does this config have an HMI associated with it? If so go back and make sure your WinPoints are correct in the points list for any revisions made in the config.

## ME++ Pseudo points
ME++ DEFAULT PSEUDOS
| Analog | Digital Input | Digital Output
1 | ONE WAY TRANSMISSION DELAY | Global DEVICES DISABLED | Global DISABLE ALL DEV
2 | # OF SUCCESSFUL TRANS W/DEV | Global POLLING DISABLED ALL DEV | Global DISABLE POLLS TO ALL DEV
3 | # OF FAILURES | Global DISABLE UNSOL RESP ALL DEV | Global DISABLE UNSOL RESP
4 | PRESENT CHANNEL | ENABLED/DISABLED DEVICE | Global POLL ALL DEV FOR CLSS DATA
5 | % OF SUCCESSFUL TRANSACTIONS | POLLING ENABLED/DISABLED | Global POLL ALL DEV FOR INTG DATA
6 |  | UNSOL RESP ENABLED/DISABLED | Global RESTART ALL DEV
7 |  | POLL FOR DATA | Global TIMESYNC ALL DEV
8 |  | REMOTE RESTART | Global CLEAR CHANNEL
9 |  | TIME SYNC REMOTE | Global CLEAR COMM STATISTIC
10 |  | PROPAGATION DELAY MEASURE | DEVICE ENABLED
11 |  | PRI COMM CHANNEL STATUS | SCHEDULED POLLS ENABLED
12 |  | SEC COMM CHANNEL STATUS | UNSOLICITED RESP ENABLED
13 |  | PRI CHANNEL IN USE | POLL DEV FOR CLASS DATA
14 |  | SEC CHANNEL IN USE | POLL DEV FOR INTEG DATA
15 |  | IIN RESTART BIT STATE | DEVICE RESTART
16 |  | IIN TROUBLE BIT STATE | TIMESYNC IN PROGRESS
17 |  |  | PROPAGATION DELAY IN PROG
18 |  |  | FORCE NEXT COM CHANNEL
19 |  |  | CLEAR COMM STATISTIC